{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["1(2)","2 (2)"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"1(2)","index":0,"n_rows":32,"n_cols":14,"rows_kept":32,"cut":false,"hidden":false,"merged":[]}
[null,null,null,null,null,"ILMAMÄÄRIEN MITTAUSPÖYTÄKIRJA"]
[]
["J.Hakanen Oy"]
["Kohde:","RAUTKALLION PÄIVÄKOTI",null,null,null,null,null,"Mittari:",null,"TSI Db Calc"]
["Osoite:","Rautkalliontie 5, 01360 VANTAA",null,null,null,null,null,"Mittauksen suoritti:",null,"Petri Eerola"]
["Kerros:",1,null,null,null,null,null,"Pvä:",null,"2012-10-31"]
[]
["Huone n:o",null,"                                                    Tuloilma l/s                               ",null,"                                 ",null,null,null,null,"Poistoilma l/s",null,null,null,"HUOM!"]
["tai tila","Venttiili","kpl","Vaadittu","Mitattu","Pa / As.",null,"Venttiili","kpl","Vaadittu","Mitattu","Pa / As"]
["102 LASTENH.","VDYc-160",2,100,100,11,null,"GRLc- 600X150",1,-100,-100,6.3]
["103 LASTENH.","VDYc-125",2,80,82,16.5,null," GRLc-600X150",1,-80,-84,4.4000000000000004]
["104 PUKEUTUMIN.","PMTC-100",1,30,30,11]
["105 SK",null,null,null,null,null,null,"KVBb-125",1,-20,-20,"143/0"]
["106 MÄRKÄ ET.",null,null,null,null,null,null,"KVBb-125",4,-100,-96,"144/3"]
["107 PESUH.",null,null,null,null,null,null,"KVBb-160",3,-90,-93,"180/-3"]
["108 HALLI","VDYc-200",1,120,120,36]
["109 HALLI","VDYc-200",1,120,120,36]
["110 PESUH/WC",null,null,null,null,null,null,"KVBb-160",4,-115,-111,"160/-2"]
["112 PUKEUTUMIN.","PMTC-100",1,30,null,"RIKKI"]
["113 LASTENH.","VDYc-160",2,100,100,11,null,"GRLc-600X150",1,-100,-101,6.4]
["114 LASTENH.","VDYc-125",2,80,80,16,null,"GRLc-600X150",1,-80,-82,4.2]
["125 WC",null,null,null,null,null,null,"KVBb-160",1,-30,-31,"142/0"]
["116 KEITTIÖ","KVI-300",1,50,"ei K-arvoa",18.5,null,"KVI-3000",1,-450,-500,17.5]
["116 KEITTIÖ","AFA+PMTC-250",2,465,492,null,null,"KVV-1500",2,-150,-301,3]
["122 HENK.K TYÖH.","PMTC-100",1,35,35,15.5,null,"KSO-100",2,-35,-34,"46/7"]
["123 HENK.K.SOS","PMTC-160",1,50,52,6,null,"KVBb-160",2,-50,-54,"75/5"]
["124 WC",null,null,null,null,null,null,"KVBb-125",1,-25,-23,"148/10"]
["124 SUIHKU",null,null,null,null,null,null,"KVBb-160",1,-30,-33,"145/-5"]
["126 AULA","VDYc-200",2,180,188,20]
[]
["KEITTIÖN TULO ON LASKENNALLINEN. MITATTU ETELÄN PUOLEISESTA RUNKOKANAVASTA 500*400 1165 l/s - LUOKAT 673 l/s"]
["KEITTIÖN KANAVISTOSTA JA PÄÄTELAITTEISTA EI SAA LUOTETTAVAA TULOSTA."]

{"sheet":"2 (2)","index":1,"n_rows":27,"n_cols":14,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
[null,null,null,null,null,"ILMAMÄÄRIEN MITTAUSPÖYTÄKIRJA"]
[]
["J.Hakanen Oy"]
["Kohde:","RAUTKALLION PÄIVÄKOTI",null,null,null,null,null,"Mittari:",null,"TSI Db Calc"]
["Osoite:","Rautkalliontie 5, 01360 VANTAA",null,null,null,null,null,"Mittauksen suoritti:",null,"Petri Eerola"]
["Kerros:",1,null,null,null,null,null,"Pvä:",null,"2012-10-31"]
[null,null,null,null,"                                 "]
["Huone n:o",null,"                                                    Tuloilma l/s                               ",null,"Mitattu",null,null,null,null,"Poistoilma l/s",null,null,null,"HUOM."]
["tai tila","Venttiili","kpl","Vaadittu",null,"Pa / As.",null,"Venttiili","kpl","Vaadittu","Mitattu","Pa / As"]
["127 NEUV/RUOK.","VDYc-125",2,80,80,16,null,"KVBb-160",3,-80,-80,"58/7"]
["129 TSTO","VDYc-100",2,30,30,15,null,"KVBb-160",1,-30,-30,"73/7"]
["130 LASTENH.","VDYc-160",2,120,121,16.5,null,"GRLc-600X150",1,-120,-121,9.1999999999999993]
["131 LASTENH.","VDYc-160",2,120,120,16.2,null,"GRLc-600X150",1,-120,"SÄHKÖ","KOTELO",null,"EDESSÄ"]
["132 LASTENH.","VDYc-160",2,120,120,16.2,null,"GRLc-600X150",1,-120,-120,9]
["133 LASTENH.","VDYc-160",2,120,120,16.2,null,"GRLc-600X150",1,-120,-124,9.5]
["135 KÄYTÄVÄ/SK",null,null,null,null,null,null,"URH-100",1,-10,-13,"172/-6"]
["136 VARASTO",null,null,null,null,null,null,"KVBb-100",1,-10,-11,"55/5"]
["137 PESUH",null,null,null,null,null,null,"KVBb-125",1,-25,-23,"108/5"]
["137 WC",null,null,null,null,null,null,"KVBb-160",2,-60,-60,"113/3"]
["138 MÄRKÄET.",null,null,null,null,null,null,"KVBb125",4,{"$f":"--94","v":94},-90,"50/15"]
["141 PUKEUTUMIN.","TRGc-600X200",1,160,160,11]
["142 LEIKKISALI","VDYc-160",3,180,181,16.3,null,"GRLc-600X150",2,-180,-184,5.3]
["143 PUKEUTUMIN.","TRGc-600X200",1,160,160,11]
["146 MÄRKÄET.",null,null,null,null,null,null,"URH-125",1,-19,-20,"116/-3"]
["146 MÄRKÄET.",null,null,null,null,null,null,"KVBb-125",3,-75,-68,"50/15"]
["147 PESUH.",null,null,null,null,null,null,"KVBb-125",1,-25,-26,"135/5"]
["147 WC",null,null,null,null,null,null,"KVBb-160",2,-60,-62,"145/0"]