{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["1(3)","2(3)","3 (3)"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"1(3)","index":0,"n_rows":24,"n_cols":14,"rows_kept":24,"cut":false,"hidden":false,"merged":[]}
[null,null,null,null,null,"ILMAMÄÄRIEN MITTAUSPÖYTÄKIRJA"]
[]
["J.Hakanen Oy"]
["Kohde:","SEUTULAN PÄIVÄKOTI",null,null,null,null,null,"Mittari:",null,"TSI Db Calc"]
["Osoite:","KATRIINANKUJA 3, 01730 VANTAA",null,null,null,null,null,"Mittauksen suoritti:",null,"Petri Eerola"]
["Kerros:","1 JA KELLARI",null,null,null,null,null,"Pvä:",null,"2012-12-13"]
[null,"TK1",null,null,null,null,null,null,null,"PK1"]
["Huone n:o",null,"                                                    Tuloilma l/s                               ",null,"                                 ",null,null,null,null,"Poistoilma l/s",null,null,null,"HUOM!"]
["tai tila","Venttiili","kpl","Vaadittu","Mitattu","Pa / As.",null,"Venttiili","kpl","Vaadittu","Mitattu","Pa / As"]
[" A RAPPU 1 KRS.","KANAVA 400*150",1,250,234,9.1999999999999993,null,null,null,null,null,null,null,"X"]
["114 KURAETEINEN",null,null,null,null,null,null,"URH-100",2,-24,-18,"12/12"]
["116 WC/PH",null,null,null,null,null,null,"URH-100",1,-15,-15,"52/9"]
["117 RYHMÄHUONE",null,null,null,null,null,null,"URH-160",2,-50,-44,"13/20"]
["118 RYHMÄHUONE",null,null,null,null,null,null,"URH-160",2,-30,-26,"15/3"]
["118 RYHMÄHUONE",null,null,null,null,null,null,"URH-160",1,-20,-18,"60/-3"]
["027 TSTO","PRA-125",1,10,10,"2,5/7",null,"KSO-100",1,-10,-11,"22/5"]
["029 OLESKELU","UNO-012-6-1,2",1,30,26,21]
["033 ASKARTELU","KANAVA 125",1,46,25,2.5,null,"KSO-125",4,-46,-40,"13/0"]
["036 VARASTO",null,null,null,null,null,null,"URH-100",1,-3,-4,"46/-12"]
["119 KEITTIÖ",null,null,null,null,null,null,"URH-160",2,-36,null,null,null,"TYRISTS."]
["119 KEITTIÖ LK.",null,null,null,null,null,null,"KANAVA-125",1,-22,-24,"2,4",null,"EI VENT."]
["037 KOK/TAUK.","UNO-012-6-1,3",1,40,36,19,null,"URH-125",2,-40,-35,"38/6"]
["035 PIENK.",null,null,null,null,null,null,"KSO-125",1,-20,-16,"16/18"]
["ALAPOHJA",null,null,null,null,null,null,"PRA-100",1,-10,-8,"50/0,5"]

{"sheet":"2(3)","index":1,"n_rows":24,"n_cols":14,"rows_kept":24,"cut":false,"hidden":false,"merged":[]}
[null,null,null,null,null,"ILMAMÄÄRIEN MITTAUSPÖYTÄKIRJA"]
[]
["J.Hakanen Oy"]
["Kohde:","SEUTULAN PÄIVÄKOTI",null,null,null,null,null,"Mittari:",null,"TSI Db Calc"]
["Osoite:","KATRIINANKUJA 3, 01730 VANTAA",null,null,null,null,null,"Mittauksen suoritti:",null,"Petri Eerola"]
["Kerros:","1 JA KELLARI",null,null,null,null,null,"Pvä:",null,"2012-12-13"]
[null,"TK2",null,null,null,null,null,null,null,"PK2"]
["Huone n:o",null,"                                                    Tuloilma l/s                               ",null,"                                 ",null,null,null,null,"Poistoilma l/s",null,null,null,"HUOM!"]
["tai tila","Venttiili","kpl","Vaadittu","Mitattu","Pa / As.",null,"Venttiili","kpl","Vaadittu","Mitattu","Pa / As"]
["B RAPPU 1 KRS.","KANAVA 400*150",1,240,254,11.1,null,null,null,null,null,null,null,"X"]
["107 KURAET.",null,null,null,null,null,null,"URH-100",2,-24,-26,"30/12"]
["108 KUIV.K.",null,null,null,null,null,null,"URH-125",1,-14,-13,"66/3"]
["109 WC/PH",null,null,null,null,null,null,"URH-100",1,-15,-15,"56/6"]
["110 RYHMÄH.",null,null,null,null,null,null,"URH-160",3,-55,-50,"37/0"]
["111 RYHMÄH.",null,null,null,null,null,null,"URH-160",3,-55,-51,"54/-3"]
["111 RYHMÄH.",null,null,null,null,null,null,"URH-100",1,-10,-11,"81/-3"]
["015 VAATEHUONE",null,null,null,null,null,null,"URH-125",2,-28,-28,"32/3"]
["017 SIIVOUS",null,null,null,null,null,null,"URH-125",1,-30,-15,"15/18"]
["018 WC",null,null,null,null,null,null,"URH-125",1,-20,-15,"14/18"]
["020 PESUH.",null,null,null,null,null,null,"URH-125",1,-16,-12,"22/3"]
["021 SOS.TILA","PRA-125",1,60,37,"7/6",null,"URH-125",2,-30,-40,"33/12"]
["023 NUKKELA","SE-125",1,28,21,"42/7"]
["024 HIEKKAL.",null,null,null,null,null,null,"URH-125",1,-10,-12,"23/3"]
["025 TYÖH.","SE-125",1,20,12,"48/3",null,"URH-100",1,-20,-12,"14/15"]

{"sheet":"3 (3)","index":2,"n_rows":24,"n_cols":14,"rows_kept":24,"cut":false,"hidden":false,"merged":[]}
[null,null,null,null,null,"ILMAMÄÄRIEN MITTAUSPÖYTÄKIRJA"]
[]
["J.Hakanen Oy"]
["Kohde:","SEUTULAN PÄIVÄKOTI",null,null,null,null,null,"Mittari:",null,"TSI Db Calc"]
["Osoite:","KATRIINANKUJA 3, 01730 VANTAA",null,null,null,null,null,"Mittauksen suoritti:",null,"Petri Eerola"]
["Kerros:","1 JA KELLARI",null,null,null,null,null,"Pvä:",null,"2012-12-13"]
[null,"TK 3",null,null,"                                 ",null,null,"PK 3"]
["Huone n:o",null,"                                                    Tuloilma l/s                               ",null,null,null,null,null,null,"Poistoilma l/s",null,null,null,"HUOM."]
["tai tila","Venttiili","kpl","Vaadittu","Mitattu","Pa / As.",null,"Venttiili","kpl","Vaadittu","Mitattu","Pa / As"]
["C RAPPU 1 KRS.","KANAVA 400*150",1,185,201,6.8,null,null,null,null,null,null,null,"X"]
["101 KURAET.",null,null,null,null,null,null,"URH-100",2,-24,-22,"120/-6"]
["102 KUIV.K.",null,null,null,null,null,null,"URH-125",1,-14,-15,"80/3"]
["103 WC/PH",null,null,null,null,null,null,"URH-100",1,-15,-14,"57/6"]
["104 RYHMÄH.",null,null,null,null,null,null,"URH-160",3,-55,-52,"57/-3"]
["105 RYHMÄH.",null,null,null,null,null,null,"URH-160",3,-55,-52,"82/-6"]
["105 RYHMÄH.",null,null,null,null,null,null,"URH-100",1,-10,-10,"138/-9"]
["004 KIRJASTO","SE-125",1,25,15,"22/7",null,"URH-100",1,-20,-6,"6/12"]
["006 VAR.",null,null,null,null,null,null,"URH-100",1,-3,-2,"5/-6"]
["008 SAUNA",null,null,null,null,null,null,"URH-100",1,-8,-5,"6/6"]
["009 PESUH.","KTS-100",1,10,7,"10/9",null,"URH-100",1,-25,-8,"10/15"]
["010 PUKUH.","KTS-125",1,30,17,"11/20",null,"URH-125",1,-15,-16,"30/6"]
["011 WC",null,null,null,null,null,null,"URH-100",1,-20,-9,"15/12"]
["013 ESIK.LK","UNO-012-12-1,2",1,40,34,"22",null,"URH-125",3,-60,-56,"35/9"]
["013 ESIK.LK","UNO-012-12-1,1",1,20,17,"22"]